Automatic Control and Protection of Renewable Energy Power Plants

Design Assignment

Project Task

The project is aimed to develop draft project of automatic control system for pitch-regulated wind power plant with parameters in the design specification (see below). During the design process, optimal PI-regulator coefficients must be defined to ensure high-quality control. The power plant is expected to be equipped with a variable-speed generator (a DFIG with slip control or PMSG).

Design project requisites

- Сover page - Project content - Specified parameters

- Functional diagram of the plant

- Differential and algebraic equations of all numerical blocks

- Block diagram of wind power plant control

- Screenshot of your Simulink - model

- m-codes of a non-linear regulator and other numerical blocks - Time diagrams (oscilloscope outputs) of wind velocity, power, pitch angle, and other values during the transient.

- Conclusions

Design Specification

| Dataset No | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rated power capacity, Pr, kW | 1000 | 100 | 3000 | 2000 | 200 | 6000 | 3300 | 300 | 7500 | 500 | 5000 |
| Rated wind velocity, Vr, m/s | 12.5 | 12 | 12.5 | 12.5 | 12 | 14 | 12.5 | 12 | 14 | 12 | 13 |
| Cut-in wind velocity Vin, m/s | 3 | 4 | 3 | 3 | 4 | 3 | 3 | 4 | 3 | 4 | 4 |
| Cut-out wind velocity Vout, m/s | 25 | 25 | 25 | 22 | 20 | 25 | 25 | 22 | 25 | 22 | 25 |
| Air density, , kg/m3 | 1.20 |  |  | 1.25 |  |  |  | 1.22 |  |  |  |
| Power coefficient, Сp | 0.45 | 0.4 | 0.49 | 0.42 | 0.38 | 0.45 | 0.42 | 0.4 | 0.45 | 0.38 | 0.4 |
| Overall efficiency, | 0.75 | 0.75 | 0.8 | 0.75 | 0.75 | 0.8 | 0.75 | 0.75 | 0.8 | 0.7 | 0.77 |
| Transient type (see below) | Turbine start |  |  | Wind gust |  |  |  | Turbine stop |  |  | Wind gust |
| Tip-speed ratio, | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 7 | 6 | 5 | 6 |
| Gearbox ratio, i | 1/50 | 1/18 | 1/40 | 1/35 | 1/22 | 1/50 | 1/45 | 1/32 | 1/35 | 1/40 | 1/48 |
| Pitch drive velocity range, d/dt, deg/s | 10 | 12 | 10 | 12 | 10 | 10 | 12 | 10 | 12 | 10 | 12 |
| Pitch angle range in regions II and III, deg | [-2; 30] |  |  |  |  |  |  |  |  |  |  |
| Pitch angle range in regions I and IV, deg | [-2; 90] |  |  |  |  |  |  |  |  |  |  |
| Anemometer time constant ТA, s | 0.12 | 0.10 |  |  |  |  |  |  | 0.15 |  |  |
| Pitch drive time constant ТD, s | 0.2 | 0.1 | 0.25 | 0.2 | 0.1 | 0.25 | 0.2 | 0.1 | 0.25 | 0.2 | 0.2 |
| Power sensor time constant ТPS, s | 0.18 |  |  |  | 0.22 |  |  |  | 0.02 |  |  |
| PI-regulator coefficient divisor, KPI | 3.5 if <0º; /2+3.5 if 0<<27º; 17 if >27º |  | 1 if <0º; /15+1 if 0<<30º; 3 if >30º |  | 2 if <0º; /5+2 if 0<<30º; 8 if >30º |  | 3.5 if <0º; /2+3.5 if 0<<27º; 17 if >27º |  | 1 if <0º; /15+1 if 0<<30º; 3 if >30º |  | 2 if <0º; /10+2 if 0<<30º; 5 if >30º |
| Initial value of proportional coefficient of regulator KP, rad*s/Nm | 5e-6 | 2e-5 | 2e-7 | 2e-7 | 1e-6 | 1e-8 | 3e-7 | 2e-6 | 1e-8 | 3e-6 | 2e-8 |
| Initial value of integral coefficient of regulator KI, rad/Nm | 1e-7 | 4e-5 | 6e-7 | 4e-7 | 2e-6 | 1.5e-8 | 9e-7 | 5e-6 | 2e-8 | 8e-6 | 1e-7 |
| Rotor moment inertia, Jrot, kg*m2 | 1e6 | 8e4 | 6e6 | 4e6 | 2e5 | 3.5e7 | 9e6 | 5e5 | 5e7 | 8e5 | 5e6 |

Transient type

Turbine start: Linear increase in average wind velocity from 2 m/s to 8 m/s within 6 seconds. Then average wind velocity is kept constant up to Т=30 s. Use a band-limited white noise with noise power 0.4 and sample time 0.8 to simulate a stochastic component of wind velocity.

Wind gust: Average wind velocity is kept equal to 10 m/s within 4 seconds. Slow down to 7 m/s when Т=8 s. Then average velocity linearly rises to 17 m/s up to Т=12 s and kept constant up to Т=20 s. Linear decrease to 7 m/s when Т=24 s. Linear increase to 10 m/s when Т=28 s. Keep average wind velocity constant to at least Т=32 s. Use a band-limited white noise with noise power 0.4 and sample time 0.8 to simulate a stochastic component of wind velocity.

Turbine stop: Average wind velocity is kept equal to 20 m/s within 5 seconds. Then average velocity linearly rises to 26 m/s up to Т=11 s and kept constant up to Т=30 s. Use a band-limited white noise with noise power 0.4 and sample time 0.8 to simulate a stochastic component of wind velocity.

| Dataset No | Student |
| --- | --- |
| 1 |  |
| 2 |  |
| 3 |  |
| 4 |  |
| 5 |  |
| 6 |  |
| 7 |  |
| 8 |  |
| 9 |  |
| 10 |  |
| 11 |  |